Consolidated Solar Battery System
Design & Build Specification — Rev 3.1
Solariver Salvage — Salt Lake City Outdoor Installation
Updated: 12× Grade B cells, 4S3P config, three-shell serviceable enclosure
# 1. System Overview
This specification covers the design and construction of a consolidated LiFePO4 battery system built from three salvaged Solariver solar pump units. All three pump controllers accept 12V DC input and are designed to operate directly from solar or battery — no boost converters are required. The system charges from three solar panel inputs (2× 40W, 1× 25W) via individual MPPT controllers and is housed in a custom 3D-printed enclosure styled as a landscape boulder for outdoor installation in Salt Lake City.
Parameter	Value
Battery chemistry	LiFePO4 (lithium iron phosphate)
Nominal bank voltage	12.8V (4S)
Cell configuration	4S3P (12× 200Ah Grade B cells)
Nominal bank capacity	~7,680 Wh (600Ah effective)
Usable capacity (80% DoD)	~6,144 Wh
Solar inputs	2× 40W + 1× 25W (105W total, 18V panels)
DC outputs	3× 12V regulated (one per pump controller)
Output fusing	2× 5A (470 GPH pumps), 1× 3A (235 GPH pump)
Thermal range (operating)	−26°C to +49°C (−15°F to 120°F)
Thermal management	Active — thermostat-controlled heat + ventilation
Max thermal system draw	20W
Design load	~65W average (all pumps running)
Autonomy without charging	66+ hours (2.7 days at worst case)
Installation	Salt Lake City, outdoors, freestanding boulder enclosure

# 2. Confirmed Solariver Hardware
Unit	Kit	Panel	Pump	Original Battery
Unit 1	470+ GPH Kit	40W, 18V	18V DC submersible, ~20–30W draw	12V / 8,000 mAh (96 Wh)
Unit 2	470+ GPH Kit	40W, 18V	18V DC submersible, ~20–30W draw	12V / 8,000 mAh (96 Wh)
Unit 3	235+ GPH Kit	25W, 18V	18V DC submersible, ~10–15W draw	12V / 6,000 mAh (72 Wh)
Totals	—	105W solar	~50–75W combined draw	264 Wh (replacing with new bank)

All three pump controllers are confirmed to operate without a battery, powered directly from the solar panel. This means they will accept any clean 12V supply without proprietary handshaking or pairing requirements. The consolidated 12.8V LiFePO4 bank is a direct drop-in replacement for all three original 12V battery packs, with approximately 23× the combined capacity.
# 3. Energy Balance & Autonomy
## 3.1 Daytime Solar Pass-Through
During daylight hours with solar available, the EPever MPPT controllers' load output terminals power the pump controllers directly from solar, bypassing the battery for the pump load. The battery only receives net surplus power after the pump load is satisfied.
Condition	Solar In	Load	Net	Notes
Full sun, all pumps	105W	~65W	+40W charging	Normal sunny day in SLC
50% cloud cover	~52W	~65W	−13W (battery)	Common afternoon cloud
Heavy overcast	~15W	~65W	−50W (battery)	Battery carries most load
Night / no sun	0W	~65W	−65W (battery)	Full battery draw

On a typical clear SLC day with 5.5 peak sun hours, solar harvests approximately 578 Wh net after powering the pumps.
## 3.2 24-Hour Energy Budget (Real Load)
Item	Power	Duration	Energy
Pumps — all three running (average)	65W	24 hrs	1,560 Wh
Thermal system (worst case, continuous)	20W	24 hrs	480 Wh
BMS + wiring losses (~10%)	—	—	204 Wh
Total consumption (worst case)	—	—	2,244 Wh
Solar offset — clear day (5.5 peak hrs)	—	—	−578 Wh
Net battery draw — clear day	—	—	1,666 Wh
Net battery draw — fully cloudy day	—	—	2,244 Wh

## 3.3 Autonomy Analysis
With 6,144 Wh usable capacity (7,680 Wh nominal at 80% DoD):
- Fully cloudy days: 6,144 ÷ 2,244 = 2.7 days autonomy — significantly exceeds 24-hour target
- With solar on a clear day: net draw of 1,666 Wh leaves 4,478 Wh reserve after 24 hours
- Consecutive cloudy days: bank can sustain approximately 66 hours at real load without any solar input
- Real load of ~65W provides massive margin over original 100W design estimate
- The 4S3P upgrade provides 50% more capacity than the original 4S2P design for approximately 35% more cell cost
# 4. Electrical Architecture
## 4.1 Voltage Design
The 12.8V nominal LiFePO4 bank (4S configuration) directly matches all three pump controllers' 12V input requirements. No boost or step-up converters are needed anywhere in the system. The three 18V solar panels each feed a dedicated MPPT controller that charges the shared 12.8V bank. Outputs are three individually fused 12V taps directly from the battery bus.
Using three separate MPPT controllers rather than one multi-input unit provides panel isolation, redundancy, and straightforward integration with the salvaged Solariver panel wiring.
## 4.2 Solar Pass-Through (Load Output)
EPever Tracer MPPT controllers include dedicated load output terminals that intelligently manage solar pass-through. When the battery is full and solar is available, pump load is powered directly from solar. When solar is insufficient, the battery supplements or takes over automatically.
- Set load output mode to 'Normal' or 'Always On' in EPever settings
- Confirm load output current rating covers your pump draw (Tracer 2210AN: 20A load output — more than sufficient)
- Wire all three pump controller inputs to the load output terminals of their respective MPPT controllers
## 4.3 Wiring Architecture
Solar panels (3× 18V) → EPever MPPT controllers (3×, isolated inputs) → load output terminals → pump controllers (3× 12V). Simultaneously: MPPT charge outputs → 12.8V LiFePO4 bank with BMS → distribution bus → fused 12V taps → pump controllers (battery backup path). The BMS sits on the battery negative bus. An 80A ANL fuse sits on the battery positive bus as close to the cells as practical.
## 4.4 Output Fusing
Output	Device	Draw	Fuse	Wire Gauge
Output 1	470 GPH pump controller	~3A	5A blade fuse	18 AWG minimum
Output 2	470 GPH pump controller	~3A	5A blade fuse	18 AWG minimum
Output 3	235 GPH pump controller	~1.5A	3A blade fuse	20 AWG minimum
Main bus	All loads + charging	60A+	80A ANL fuse	8 AWG

# 5. Battery Bank
## 5.1 Why LiFePO4
LiFePO4 is strongly preferred over LiPo for this application. LiPo cells perform poorly in cold temperatures, require more careful management to avoid thermal runaway, and have significantly shorter cycle lives (300–500 cycles vs 2,000+ for LiFePO4). For an unattended outdoor installation in Salt Lake City's climate extremes, LiFePO4's chemical stability, cold-temperature tolerance, and long service life make it the clear choice.
## 5.2 Why Grade B Cells
Grade B LiFePO4 cells are typically units that tested slightly below the manufacturer's rated capacity threshold (e.g., 185–195Ah on a 200Ah cell), were pulled from new but unsold battery packs, or have minor cosmetic defects that do not affect performance. For this application's moderate duty cycle (one partial daily cycle, rarely below 60% SOC on clear days), the practical difference from Grade A is negligible.
Purchasing 12 Grade B cells provides matching headroom — cells can be individually capacity-tested and matched into parallel groups of 3 within 2–3% capacity. The cost savings of approximately $280–360 vs Grade A makes this the optimal value choice. If all 12 cells match well, the pack can be built as 4S3P for 50% more capacity than the original 4S2P design.
## 5.3 Cell Configuration
12× 200Ah 3.2V LiFePO4 prismatic cells in 4S3P:
- 4S = 4 cells in series = 12.8V nominal (direct match for 12V pump controllers)
- 3P = 3 parallel strings = 600Ah effective
- Total bank: 12.8V × 600Ah = 7,680 Wh nominal
- Usable at 80% DoD: ~6,144 Wh — 2.7× the worst-case 24-hour draw
Recommended sources: EVE LF280K or CATL/CALB 200Ah prismatic cells, Grade B. Budget approximately $45–75 per cell ($540–900 for 12 cells). Cell dimensions approximately 174mm × 71mm × 207mm each; 4S3P stack occupies roughly 350mm × 215mm × 315mm.
## 5.4 Parallel Matching for 3P Strings
⚠ All three cells in each parallel group must be matched within 2–3% capacity and have similar internal resistance. Mismatched parallel cells cause uneven current distribution, accelerated aging, and potential thermal issues.
- Capacity-test all 12 cells individually with a full charge/discharge cycle
- Sort by measured capacity (highest to lowest)
- Group into 4 sets of 3, each set within 2–3% of each other
- Also compare internal resistance (IR) — cells in the same parallel group should be within 10–15% IR of each other
- If any cell cannot be matched into a group, set it aside as a spare
- If only 8–11 cells match well, fall back to 4S2P with the best 8 and keep the rest as spares
## 5.5 Critical Temperature Rules
⚠ These constraints are enforced by the BMS and thermostat system and must never be bypassed.
- Charging prohibited below 0°C (32°F) — causes lithium plating and permanent cell damage
- Discharging acceptable down to −20°C (−4°F) at reduced current
- Optimal operating range: 10°C to 35°C (50°F to 95°F)
- Maximum charge temperature: 45°C (113°F)
- BMS charge-inhibit port wired to temperature probe — enforces 0°C charge floor automatically
# 6. Thermal Management System
## 6.1 Salt Lake City Climate
SLC winters regularly reach −15°F (−26°C) and summers push 105°F (40°C+). The approach is insulation-first, with active thermostat-controlled heating and ventilation within the 20W power budget. The larger 4S3P battery provides even more thermal energy reserve for extended winter heating.
## 6.2 Heating (Winter)
A 12V PTC ceramic heater element (10–15W) inside the battery zone, wired to the thermostat heating relay. PTC elements are self-regulating — resistance increases as temperature rises, naturally throttling power draw.
- Heater ON below +5°C (41°F)
- Heater OFF at +10°C (50°F)
- BMS charge inhibit released only above 0°C (32°F)
## 6.3 Cooling (Summer)
Forced ventilation via a 12V brushless fan (3–5W) in the electronics outer zone. Reflective/light-colored enclosure exterior reduces solar heat gain. Note: the larger 4S3P cell mass provides more thermal inertia, which is beneficial — the pack heats and cools more slowly, damping temperature swings.
- Fan ON above +35°C (95°F) inside battery zone
- Fan OFF below +30°C (86°F)
## 6.4 Thermostat Setpoints
Function	Threshold	Action
Heating ON	+5°C (41°F)	PTC heater activates
Heating OFF	+10°C (50°F)	PTC heater deactivates
Cooling ON	+35°C (95°F)	Fan activates
Cooling OFF	+30°C (86°F)	Fan deactivates
Charge inhibit (BMS)	0°C (32°F)	MPPT charge disconnected via BMS temp port

# 7. Enclosure Design
## 7.1 Overview — Three-Shell Serviceable Architecture
The enclosure uses a three-shell design that separates structural insulation from serviceable components. Every electrical component is removable and replaceable without destroying the enclosure. No component is permanently entombed in foam.
⚠ Design principle: Foam is only structural/thermal. No wires, no components, and no connections exist inside the foam cavity. Everything serviceable lives inside the inner service shell, accessed through insulated service panels.
## 7.2 Shell Layers (Outside → Inside)
- Shell 1 — Outer boulder: ASA filament, stone-textured. Cosmetic, weather barrier, structural outer wall. Permanently solvent-welded.
- Foam cavity (25–40mm): 2 lb closed-cell polyurethane pour foam between shells 1 and 2. Insulation + structural rigidity. Permanent — contains NO components or wiring.
- Shell 2 — Middle structural shell: ASA filament. Inner wall of foam cavity, mounting surface. Permanently solvent-welded to outer shell before foam pour.
- Shell 3 — Inner service shell: ASA filament, bolted (not welded) to shell 2. Houses ALL components. Accessible via removable insulated panels.
## 7.3 Cable Routing Through Foam Cavity
All cables between the exterior and the inner service shell pass through printed ASA conduit sleeves embedded in the foam cavity. Conduits are installed before the foam pour. Foam bonds around the outside of each conduit, but the interior remains hollow and clear. Wires can be pulled through at any time for replacement. PG cable glands thread into the outer end of each conduit for IP68 weather sealing.
## 7.4 Component Mounting (All Removable)
Every component mounts mechanically to the inner service shell or to DIN rail / mounting plates bolted to it. No component is glued, foamed, or permanently bonded. Cells sit on a compression cradle accessible through the battery access panel. Electronics mount on DIN rail or standoffs accessible through the electronics access panel.
## 7.5 Service Panels
Two removable access panels (battery zone and electronics zone) are printed ASA plates that sit in recessed frames with EPDM gasket seals. Behind each panel, a removable rigid foam insulation board (25mm XPS or polyiso) provides thermal isolation. The insulation is friction-fit and removed during service. Battery access panel opening: minimum 360mm × 220mm clear for cell stack removal. Electronics access panel: minimum 200mm × 180mm for MPPT controller removal.
## 7.5 Vent Ports
Two filtered vent ports on lower back face with printed ASA baffles preventing direct water ingress. Removable foam plugs available for winter to reduce heat loss.
## 7.6 Exterior Finish
Print in mid-gray ASA base. Apply stone-texture spray paint (Rust-Oleum Stone or similar) to match existing landscape features. UV-resistant clear topcoat. Light/reflective color is important — a dark boulder in SLC summer sun would significantly increase thermal load.
## 7.7 Mounting
Flat printed base with four heat-set M8 threaded inserts for optional anchor bolts. System weight approximately 28–32kg (cells alone ~24kg) — inherently stable freestanding.
# 8. Salvage from Solariver Units
Item	Action	Notes
Solar panels (40W × 2, 25W × 1)	Reuse all three	Test Voc and Isc before integration.
Pump controllers / timer boards	Reuse all three	Confirmed compatible with external 12V supply.
Pump units	Reuse all three	Powered by controllers; no changes.
Panel mounting hardware	Reuse	Brackets, tilt adjusters, fasteners.
Wiring harnesses and MC4 connectors	Reuse where possible	Inspect insulation; replace cracked runs.
Original batteries (12V SLA or LiPo)	Discard / recycle	Hazardous waste disposal.
Original PWM charge controllers	Discard	Replace with EPever MPPT units.

# 9. Recommended Build Sequence
Step 1 — Test salvaged panels: Measure Voc (open circuit) and Isc (short circuit) on each panel in direct sun. Confirm usable output on all three. Expected: ~21–22V Voc, 1–2.3A Isc depending on wattage.
Step 2 — Test pump controllers with external 12V: Before building anything, power each pump controller from a bench 12V supply and confirm normal pump operation.
Step 3 — Grade and test all 12 LiFePO4 cells: Capacity-test each cell individually. Match cells into parallel groups of 3 within 2–3% capacity and similar internal resistance. If fewer than 12 match, fall back to 4S2P with the best 8.
Step 4 — Build and bench-test battery pack: Wire 4S3P, connect BMS, verify cell voltages balance, confirm BMS protection triggers.
Step 5 — Build and bench-test full electronics stack: Wire EPever MPPT controllers, distribution bus, fuse block, and thermostat. Verify solar pass-through on load output terminals.
Step 6 — 24-hour bench endurance test: Run all three pump controllers at full load for 24 hours without solar input. Target: >3,900 Wh remaining (>50% SOC). The 4S3P pack should finish well above 60% SOC.
Step 7 — Design enclosure around confirmed component dimensions: Use actual measured 4S3P cell stack dimensions. Design boulder in CAD, segment for Prusa Core One bed size.
Step 8 — Print shells and conduit sleeves: Print all three shells, access panel covers, cable conduit sleeves, and vent conduit sleeves in ASA.
Step 9 — Assemble outer structure and pour foam: Solvent-weld shell 1 and shell 2 with conduit sleeves positioned between them. Verify all conduits are clear with pull wires. Pour foam into cavity. This is the only irreversible step — but no components live in the foam.
Step 10 — Install inner service shell and mount components: Bolt (not weld) inner service shell to middle shell. Mount ALL components mechanically — no glue, no foam. Route cables through conduit sleeves. Every component must be removable through an access panel.
Step 11 — Install insulation and close access panels: Cut rigid foam insulation boards for each panel opening. Friction-fit behind panels. Apply EPDM gasket. Bolt access panels closed. Install vent baffles.
Step 12 — Finish and install: Apply stone-texture paint and UV topcoat. Place in position, connect panels and pump controllers, verify operation. Confirm serviceability by opening and re-closing one access panel.
# 10. Full Component List
Component	Qty	Specification	Est. Cost
LiFePO4 prismatic cells	12	200Ah 3.2V Grade B (EVE/CATL/CALB)	$540–900
4S LiFePO4 BMS	1	60A+, temp cutoff, balance (JK BMS or Daly)	$40–80
EPever Tracer MPPT controller	3	2210AN — 18V input, 12.8V LiFePO4, 20A load out	$35–55 ea.
Distribution bus bar	1	12V pos + neg, 6+ terminals	$15–25
3-way blade fuse block	1	With 2× 5A + 1× 3A fuses	$8–15
80A ANL fuse + holder	1	Weatherproof, on positive bus	$10–18
STC-1000 thermostat controller	1	Dual stage, relay output, probe included	$12–18
PTC ceramic heater element	1	12V, 10–15W, self-limiting	$8–15
12V brushless fan	1	80–120mm, 3–5W	$8–12
8 AWG tinned marine wire	~6m	Main bus runs (slightly longer for 3P)	$18–30
18–20 AWG tinned marine wire	~10m	Branch runs to pump controllers	$10–18
PG cable glands (assorted)	6–8	PG9 and PG13.5	$10–20
EPDM foam tape (gasket)	~1m	3–5mm closed-cell, self-adhesive	$5–10
Stainless M4 bolts + heat-set inserts	8–10 sets	Service panel fasteners	$8–15
Stainless M8 inserts + anchor hardware	4 sets	Base anchoring (optional)	$8–12
2-part pour foam kit	1	2 lb closed-cell, 1–2 gallon kit	$20–35
ASA filament	5–7 kg	Larger boulder for 4S3P stack	$80–175
Stone texture paint + UV topcoat	1 set	Exterior masonry / stone spray, light color	$20–35
MC4 connectors (pairs)	6	For panel-to-controller connections	$10–18
Cell compression kit	1	Threaded rod, end plates for 4S3P stack	$15–30
Nickel-plated copper bus bars	12	Cell-to-cell connections (more for 3P)	$15–25

Estimated total (excluding salvaged panels, pump units, and controllers): $900–$1,450.
This represents a modest cost reduction from Rev 2 ($1,000–$1,550) despite 50% more cell capacity, thanks to Grade B cell pricing. The cell pack at $540–900 represents approximately 60% of total cost.
Items eliminated vs Rev 1: 2× 18V boost converters (no longer needed — all outputs are 12V native).
# 11. Safety Notes
⚠ Review ALL safety notes before beginning any electrical work. LiFePO4 cells at 200Ah can deliver thousands of amps into a short circuit.
- Never short cell terminals — even briefly. Cover all terminals with tape when not actively being connected.
- Always connect the BMS before connecting any load or charge source to the pack.
- Do not charge below 0°C — the thermostat/BMS interlock exists for this reason. Never bypass it.
- The foam pour (step 9) is irreversible — but no components live in the foam cavity. Verify all conduit sleeves are clear with pull wires before and after foam pour.
- Every component must remain removable through an access panel. Never glue, foam, or permanently bond any electrical component to the enclosure.
- Test thermostat, heater, and fan independently during step 10 before closing access panels in step 11.
- The ANL fuse on the positive bus is your primary fault protection. Install within 30cm of battery positive terminal.
- When disposing of old Solariver batteries, take to a battery recycling facility.
- With 3P parallel strings, ensure all three cells in each group are connected simultaneously. Never connect a charged cell in parallel with a discharged cell — the equalization current can exceed safe levels.
# 12. EPever MPPT Configuration
All three Tracer 2210AN controllers must be programmed with identical LiFePO4 battery settings. Configuration is unchanged from Rev 2 — the larger battery capacity does not affect charge controller settings since voltage is the same.
Parameter	Value	Notes
Battery Type	USER (LiFePO4)	Select 'USER' then set voltages below
Charging Limit Voltage	14.4V	Absorption (3.60V/cell)
Float Voltage	13.6V	3.40V/cell — gentle maintenance float
Low Voltage Disconnect	11.2V	Cut load (2.80V/cell)
Temperature Compensation	0 mV/°C/2V	CRITICAL — disable for LiFePO4
Load Working Mode	Always ON	Or 'Light ON/OFF' for daytime-only
Equalization Duration	0 min	Disable EQ cycling for LiFePO4
Boost Duration	120 min	Time at absorption before float

⚠ Temperature Compensation must be set to 0 mV/°C/2V for LiFePO4. The default lead-acid compensation will overcharge LiFePO4 cells in cold weather, causing permanent damage.
Document prepared with Claude — Rev 3. Verify all electrical specifications against component datasheets before construction.